## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1 | 0 | 40 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
2 | 2 | 0.98 | 0 | 5.45 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
3 | 2 | 0.983 | 0 | 6.5 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
4 | 2 | 0.997 | 0 | 6.32 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
5 | 2 | 1.011 | 0 | 5.05 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
6 | 2 | 1.05 | 0 | 7 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
7 | 2 | 1.063 | 0 | 5.6 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
8 | 2 | 1.03 | 0 | 5.4 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
9 | 2 | 1.025 | 0 | 8 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
10 | 2 | 1.01 | 0 | 5 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
11 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
12 | 2 | 1.0156 | 0 | 13.5 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
13 | 2 | 1.011 | 0 | 35.91 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
14 | 2 | 1 | 0 | 17.85 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
15 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
16 | 2 | 1.045 | 0 | 2.5 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
17 | 3 | 1 | 0 | -60 | -3 | 0 | 0 | -9999 | 9999 | 1 | 1
18 | 3 | 1 | 0 | -24.7 | -1.23 | 0 | 0 | -9999 | 9999 | 1 | 1
19 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
20 | 3 | 1 | 0 | -6.8 | -1.03 | 0 | 0 | -9999 | 9999 | 1 | 1
21 | 3 | 1 | 0 | -2.74 | -1.15 | 0 | 0 | -9999 | 9999 | 1 | 1
22 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
23 | 3 | 1 | 0 | -2.48 | -0.85 | 0 | 0 | -9999 | 9999 | 1 | 1
24 | 3 | 1 | 0 | -3.09 | 0.92 | 0 | 0 | -9999 | 9999 | 1 | 1
25 | 3 | 1 | 0 | -2.24 | -0.47 | 0 | 0 | -9999 | 9999 | 1 | 1
26 | 3 | 1 | 0 | -1.39 | -0.17 | 0 | 0 | -9999 | 9999 | 1 | 1
27 | 3 | 1 | 0 | -2.81 | -0.76 | 0 | 0 | -9999 | 9999 | 1 | 1
28 | 3 | 1 | 0 | -2.06 | -0.28 | 0 | 0 | -9999 | 9999 | 1 | 1
29 | 3 | 1 | 0 | -2.84 | -0.27 | 0 | 0 | -9999 | 9999 | 1 | 1
30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
31 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
32 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
33 | 3 | 1 | 0 | -1.12 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
34 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
35 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
36 | 3 | 1 | 0 | -1.02 | 0.1946 | 0 | 0 | -9999 | 9999 | 1 | 1
37 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
38 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
39 | 3 | 1 | 0 | -2.67 | -0.126 | 0 | 0 | -9999 | 9999 | 1 | 1
40 | 3 | 1 | 0 | -0.6563 | -0.2353 | 0 | 0 | -9999 | 9999 | 1 | 1
41 | 3 | 1 | 0 | -10 | -2.5 | 0 | 0 | -9999 | 9999 | 1 | 1
42 | 3 | 1 | 0 | -11.5 | -2.5 | 0 | 0 | -9999 | 9999 | 1 | 1
43 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
44 | 3 | 1 | 0 | -2.6755 | -0.0484 | 0 | 0 | -9999 | 9999 | 1 | 1
45 | 3 | 1 | 0 | -2.08 | -0.21 | 0 | 0 | -9999 | 9999 | 1 | 1
46 | 3 | 1 | 0 | -1.507 | -0.285 | 0 | 0 | -9999 | 9999 | 1 | 1
47 | 3 | 1 | 0 | -2.0312 | -0.3259 | 0 | 0 | -9999 | 9999 | 1 | 1
48 | 3 | 1 | 0 | -2.412 | -0.022 | 0 | 0 | -9999 | 9999 | 1 | 1
49 | 3 | 1 | 0 | -1.64 | -0.29 | 0 | 0 | -9999 | 9999 | 1 | 1
50 | 3 | 1 | 0 | -1 | 1.47 | 0 | 0 | -9999 | 9999 | 1 | 1
51 | 3 | 1 | 0 | -3.37 | 1.22 | 0 | 0 | -9999 | 9999 | 1 | 1
52 | 3 | 1 | 0 | -1.58 | -0.3 | 0 | 0 | -9999 | 9999 | 1 | 1
53 | 3 | 1 | 0 | -2.527 | -1.1856 | 0 | 0 | -9999 | 9999 | 1 | 1
54 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
55 | 3 | 1 | 0 | -3.22 | -0.02 | 0 | 0 | -9999 | 9999 | 1 | 1
56 | 3 | 1 | 0 | -2 | -0.736 | 0 | 0 | -9999 | 9999 | 1 | 1
57 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
58 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
59 | 3 | 1 | 0 | -2.34 | -0.84 | 0 | 0 | -9999 | 9999 | 1 | 1
60 | 3 | 1 | 0 | -2.088 | -0.708 | 0 | 0 | -9999 | 9999 | 1 | 1
61 | 3 | 1 | 0 | -1.04 | -1.25 | 0 | 0 | -9999 | 9999 | 1 | 1
62 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
63 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
64 | 3 | 1 | 0 | -0.09 | -0.88 | 0 | 0 | -9999 | 9999 | 1 | 1
65 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
66 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | -9999 | 9999 | 1 | 1
67 | 3 | 1 | 0 | -3.2 | -1.53 | 0 | 0 | -9999 | 9999 | 1 | 1
68 | 3 | 1 | 0 | -3.29 | -0.32 | 0 | 0 | -9999 | 9999 | 1 | 1

## Device
This sheet summarizes the devices connected to buses.
Bus number | Device type | Device parameters
1 | 1 | 1000 | 100 | 0.001 | 0.0002
2 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
3 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
4 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
5 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
6 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
7 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
8 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
9 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
10 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
11 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
12 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
13 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
14 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
15 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
16 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
17 | 1 | 1000 | 100 | 0.001 | 0.0002
18 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
19 | 100
20 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
21 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
22 | 100
23 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
24 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
25 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
26 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
27 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
28 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
29 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
30 | 100
31 | 100
32 | 100
33 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
34 | 100 |  |  | 0.05 | 0.01 | 10 | 2000
35 | 100 |  |  | 0.05 | 0.01 | 10 | 2000
36 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
37 | 100 |  |  | 0.05 | 0.01 | 10 | 2000
38 | 100 |  |  | 0.05 | 0.01 | 10 | 2000
39 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
40 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
41 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
42 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
43 | 100 |  |  | 0.05 | 0.01 | 10 | 2000
44 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
45 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
46 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
47 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
48 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
49 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
50 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
51 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
52 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
53 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
54 | 100
55 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
56 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
57 | 100
58 | 100
59 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
60 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
61 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
62 | 100
63 | 100
64 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
65 | 100
66 | 100
67 | 11 |  |  | 0.05 | 0.01 | 10 | 2000
68 | 11 |  |  | 0.05 | 0.01 | 10 | 2000

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
16 | 54 | 1e-07 | 0.0181 | 0 | 0 | 1.025
2 | 58 | 1e-07 | 0.025 | 0 | 0 | 1.07
3 | 62 | 1e-07 | 0.02 | 0 | 0 | 1.07
4 | 19 | 0.0007 | 0.0142 | 0 | 0 | 1.07
5 | 20 | 0.0009 | 0.018 | 0 | 0 | 1.009
6 | 22 | 1e-07 | 0.0143 | 0 | 0 | 1.025
7 | 23 | 0.0005 | 0.0272 | 0 | 0 | 1
8 | 25 | 0.0006 | 0.0232 | 0 | 0 | 1.025
9 | 29 | 0.0008 | 0.0156 | 0 | 0 | 1.025
10 | 31 | 1e-07 | 0.026 | 0 | 0 | 1.04
11 | 32 | 1e-07 | 0.013 | 0 | 0 | 1.04
12 | 36 | 1e-07 | 0.0075 | 0 | 0 | 1.04
13 | 17 | 1e-07 | 0.0033 | 0 | 0 | 1.04
14 | 41 | 1e-07 | 0.0015 | 0 | 0 | 1
15 | 42 | 1e-07 | 0.0015 | 0 | 0 | 1
1 | 18 | 1e-07 | 0.003 | 0 | 0 | 1
17 | 36 | 0.0005 | 0.0045 | 0.32 | 0 | 1
18 | 49 | 0.0076 | 0.1141 | 1.16 | 0 | 1
18 | 50 | 0.0012 | 0.0288 | 2.06 | 0 | 1
19 | 68 | 0.0016 | 0.0195 | 0.304 | 0 | 1
20 | 19 | 0.0007 | 0.0138 | 0 | 0 | 1.06
21 | 68 | 0.0008 | 0.0135 | 0.2548 | 0 | 1
22 | 21 | 0.0008 | 0.014 | 0.2565 | 0 | 1
23 | 22 | 0.0006 | 0.0096 | 0.1846 | 0 | 1
24 | 23 | 0.0022 | 0.035 | 0.361 | 0 | 1
24 | 68 | 0.0003 | 0.0059 | 0.068 | 0 | 1
25 | 54 | 0.007 | 0.0086 | 0.146 | 0 | 1
26 | 25 | 0.0032 | 0.0323 | 0.531 | 0 | 1
27 | 37 | 0.0013 | 0.0173 | 0.3216 | 0 | 1
27 | 26 | 0.0014 | 0.0147 | 0.2396 | 0 | 1
28 | 26 | 0.0043 | 0.0474 | 0.7802 | 0 | 1
29 | 26 | 0.0057 | 0.0625 | 1.029 | 0 | 1
29 | 28 | 0.0014 | 0.0151 | 0.249 | 0 | 1
30 | 53 | 0.0008 | 0.0074 | 0.48 | 0 | 1
30 | 61 | 0.00095 | 0.00915 | 0.58 | 0 | 1
31 | 30 | 0.0013 | 0.0187 | 0.333 | 0 | 1
31 | 53 | 0.0016 | 0.0163 | 0.25 | 0 | 1
32 | 30 | 0.0024 | 0.0288 | 0.488 | 0 | 1
33 | 32 | 0.0008 | 0.0099 | 0.168 | 0 | 1
34 | 33 | 0.0011 | 0.0157 | 0.202 | 0 | 1
34 | 35 | 0.0001 | 0.0074 | 0 | 0 | 0.946
36 | 34 | 0.0033 | 0.0111 | 1.45 | 0 | 1
36 | 61 | 0.0011 | 0.0098 | 0.68 | 0 | 1
37 | 68 | 0.0007 | 0.0089 | 0.1342 | 0 | 1
38 | 31 | 0.0011 | 0.0147 | 0.247 | 0 | 1
38 | 33 | 0.0036 | 0.0444 | 0.693 | 0 | 1
40 | 41 | 0.006 | 0.084 | 3.15 | 0 | 1
40 | 48 | 0.002 | 0.022 | 1.28 | 0 | 1
41 | 42 | 0.004 | 0.06 | 2.25 | 0 | 1
42 | 18 | 0.004 | 0.06 | 2.25 | 0 | 1
43 | 17 | 0.0005 | 0.0276 | 0 | 0 | 1
44 | 39 | 1e-07 | 0.0411 | 0 | 0 | 1
44 | 43 | 0.0001 | 0.0011 | 0 | 0 | 1
45 | 35 | 0.0007 | 0.0175 | 1.39 | 0 | 1
45 | 39 | 1e-07 | 0.0839 | 0 | 0 | 1
45 | 44 | 0.0025 | 0.073 | 0 | 0 | 1
46 | 38 | 0.0022 | 0.0284 | 0.43 | 0 | 1
47 | 53 | 0.0013 | 0.0188 | 1.31 | 0 | 1
48 | 47 | 0.00125 | 0.0134 | 0.8 | 0 | 1
49 | 46 | 0.0018 | 0.0274 | 0.27 | 0 | 1
51 | 45 | 0.0004 | 0.0105 | 0.72 | 0 | 1
51 | 50 | 0.0009 | 0.0221 | 1.62 | 0 | 1
52 | 37 | 0.0007 | 0.0082 | 0.1319 | 0 | 1
52 | 55 | 0.0011 | 0.0133 | 0.2138 | 0 | 1
54 | 53 | 0.0035 | 0.0411 | 0.6987 | 0 | 1
55 | 54 | 0.0013 | 0.0151 | 0.2572 | 0 | 1
56 | 55 | 0.0013 | 0.0213 | 0.2214 | 0 | 1
57 | 56 | 0.0008 | 0.0128 | 0.1342 | 0 | 1
58 | 57 | 0.0002 | 0.0026 | 0.0434 | 0 | 1
59 | 58 | 0.0006 | 0.0092 | 0.113 | 0 | 1
60 | 57 | 0.0008 | 0.0112 | 0.1476 | 0 | 1
60 | 59 | 0.0004 | 0.0046 | 0.078 | 0 | 1
61 | 60 | 0.0023 | 0.0363 | 0.3804 | 0 | 1
63 | 58 | 0.0007 | 0.0082 | 0.1389 | 0 | 1
63 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
63 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
65 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
65 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
66 | 56 | 0.0008 | 0.0129 | 0.1382 | 0 | 1
66 | 65 | 0.0009 | 0.0101 | 0.1723 | 0 | 1
67 | 66 | 0.0018 | 0.0217 | 0.366 | 0 | 1
68 | 67 | 0.0009 | 0.0094 | 0.171 | 0 | 1
27 | 53 | 0.032 | 0.32 | 0.41 | 0 | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 1
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0