## PowerFlow
This sheet summarizes the parameters for power flow analysis
Notes:
type: 1-slack bus, 2-PV bus, 3-PQ bus
The bus 1 HAVE TO be the slack bus, i.e., type-1 bus.
PGi and QGi are in generator convention. PLi and QLi are in load convention.
For active device (SG, VSI, etc), please use PGI and QGi. For load, please use PLi and QLi.
Data:
bus | type | Vsp | theta | PGi | QGi | PLi | QLi | Qmin | Qmax
1 | 1 | 1.06 | 0 | 10 | 0 | 0 | 0 | -200 | 200
2 | 2 | 1.045 | 0 | 40 | 0 | 21.7 | 12.7 | -40 | 50
3 | 2 | 1.01 | 0 | 0 | 10 | 94.2 | 19 | 0 | 40
4 | 3 | 1 | 0 | 0 | 0 | 47.8 | -3.9 | 0 | 0
5 | 3 | 1 | 0 | 0 | 0 | 7.6 | 1.6 | 0 | 0
6 | 2 | 1.07 | 0 | 0 | 10 | 11.2 | 7.5 | -6 | 24
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1.09 | 0 | 0 | 10 | 0 | 0 | -6 | 24
9 | 3 | 1 | 0 | 0 | 0 | 29.5 | 16.6 | 0 | 0
10 | 3 | 1 | 0 | 0 | 0 | 9 | 5.8 | 0 | 0
11 | 3 | 1 | 0 | 0 | 0 | 3.5 | 1.8 | 0 | 0
12 | 3 | 1 | 0 | 0 | 0 | 6.1 | 1.6 | 0 | 0
13 | 3 | 1 | 0 | 0 | 0 | 13.5 | 5.8 | 0 | 0
14 | 3 | 1 | 0 | 0 | 0 | 14.9 | 5 | 0 | 0

## Device
This sheet summarizes the devices connected to buses.
Notes:
For each bus, at least ONE and only ONE device can be connected.
The buses and corresponding devices CAN be listed below in arbitrary order.
If the parameters are left to blank, the default paramters will be used.
The red highlighted devices are not available currently.
For adding passive load, please use PLi and QLi in the "PowerFlow" sheet.
Data Form with Default Values:
| 0-10, Synchronous Generator | H (pu) = 3.5 | D (pu) = 5 | wL (pu) = 0.03 | R (pu) = 0.01
0, Synchronous Generator
%%%
| 10-19, Grid-Following VSI | Vdc (pu) = 2.5 | Cdc (pu) = 1.25 | wL (pu) = 0.03 | R (pu) = 0.01 | Bandwidth vdc (Hz) = 20 | Bandwidth PLL (Hz) = 20 | Bandwidth idq (Hz) = 500
10, PLL-Controlled VSI
%%%
20-29, Grid-Forming VSI
21, Droop-Controlled VSI
%%%
90, Infinite Bus (Short Circuit in Small-Signal)
%%%
100, Floating Bus (Open Circuit)
%%%
Data:
bus number | type number | parameters
1 | 0 | 35 | 10 | 0.3 | 0.1
2 | 0 | 3.5 | 1 | 0.3 | 0.1
3 | 0 | 3.5 | 10 | 0.3 | 0.1
4 | 100
5 | 100
6 | 0 | 3.5 | 10 | 0.3 | 0.1
7 | 100
8 | 0 | 3.5 | 10 | 0.3 | 0.1
9 | 100
10 | 100
11 | 100
12 | 100
13 | 100
14 | 100

## Basic
This sheet summarizes basic settings
Data:
Samping frequency (Hz) | 40000
Base Frequency (Hz) | 60
Base Power (VA) | 100
Base Voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
Notes:
Zbranch = R+wL+1/(wC+G)
The transformer is added between FromBus and Zbranch
The branches can be listed in arbitrary order.
Mutual branch HAS TO be RL.
Self branch HAS TO be GC.
All self branch HAT TO be set, even with a very small value of G.
Data:
from bus | to bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns Ratio (pu)
1 | 2 | 0.01938 | 0.05917 | 0 | inf | 1
1 | 5 | 0.05403 | 0.22304 | 0 | inf | 1
2 | 3 | 0.04699 | 0.19797 | 0 | inf | 1
2 | 4 | 0.05811 | 0.17632 | 0 | inf | 1
2 | 5 | 0.05695 | 0.17388 | 0 | inf | 1
3 | 4 | 0.06701 | 0.17103 | 0 | inf | 1
4 | 5 | 0.01335 | 0.04211 | 0 | inf | 1
4 | 7 | 1e-20 | 0.20912 | 0 | inf | 1
4 | 9 | 1e-20 | 0.55618 | 0 | inf | 1
5 | 6 | 1e-20 | 0.25202 | 0 | inf | 1
6 | 11 | 0.09498 | 0.1989 | 0 | inf | 1
6 | 12 | 0.12291 | 0.25581 | 0 | inf | 1
6 | 13 | 0.06615 | 0.13027 | 0 | inf | 1
7 | 8 | 1e-20 | 0.17615 | 0 | inf | 1
7 | 9 | 1e-20 | 0.11001 | 0 | inf | 1
9 | 10 | 0.03181 | 0.0845 | 0 | inf | 1
9 | 14 | 0.12711 | 0.27038 | 0 | inf | 1
10 | 11 | 0.08205 | 0.19207 | 0 | inf | 1
12 | 13 | 0.22092 | 0.19988 | 0 | inf | 1
13 | 14 | 0.17093 | 0.34802 | 0 | inf | 1
1 | 1 | 0 | 0 | 0.051 | 0 | 1
2 | 2 | 0 | 0 | 0.0562 | 0 | 1
3 | 3 | 0 | 0 | 0.0283 | 0 | 1
4 | 4 | 0 | 0 | 0.0234 | 0 | 1
5 | 5 | 0 | 0 | 0.0419 | 0 | 1
6 | 6 | 0 | 0 | 1e-20 | 0 | 1
7 | 7 | 0 | 0 | 1e-20 | 0 | 1
8 | 8 | 0 | 0 | 1e-20 | 0 | 1
9 | 9 | 0 | 0 | 0.19 | 0 | 1
10 | 10 | 0 | 0 | 1e-20 | 0 | 1
11 | 11 | 0 | 0 | 1e-20 | 0 | 1
12 | 12 | 0 | 0 | 1e-20 | 0 | 1
13 | 13 | 0 | 0 | 1e-20 | 0 | 1
14 | 14 | 0 | 0 | 1e-20 | 0 | 1

## NetworkLine_IEEE Form
This sheet summarizes the parameters for network line impedance in IEEE form.
Notes:
If using this sheet, please set enable from 0 to 1, then this sheet will over-write "NetworkLine"
Enable:
0
Data:
from bus | to bus | R (pu) | X (pu) | B/2 (pu) | G/2 (pu) | Turns Ratio
1 | 2 | 0.01938 | 0.05917 | 0.0264 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0246 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0219 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.017 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0173 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0064 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 1
4 | 7 | 0 | 0.20912 | 0 | 0 | 0.978
4 | 9 | 0 | 0.55618 | 0 | 0 | 0.969
5 | 6 | 0 | 0.25202 | 0 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 1
7 | 8 | 0 | 0.17615 | 0 | 0 | 1
7 | 9 | 0 | 0.11001 | 0 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 1

## Advanced Setting
This sheets summaries advanced settings for the toolbox
Data:
Discretization Method | 2 | 1-Forward Eular, 2-Hybrid Euler-Trapezoidal, 3-Virtual damping
Linearization Times | 1 | 1-Initial step, 2-Every step
Discre Damping Flag | 1 | 1-With virtual damping resistor, 2-Without virtual damping resistor
DirectFeedthrough | 0 | 1-Yes, 2-No
Enable_SimulinkModel | 1 | 1-Enable, 2-Disable
Enable_PlotPole | 1 | 1-Enable, 2-Disable
Enable_PlotAdmittance | 1 | 1-Enable, 2-Disable
Enable_PrintOutput | 1 | 1-Enable, 2-Disable
Enable_PlotSwing | 1 | 1-Enable, 2-Disable